## PFD
|  |  |  | BLR1 M | 60.0025
|  |  |  | BLR2 M | 40.0017
|  |  |  | BLR3 M | 20.0008
121.2051
120.0051
[6 empty] | 3214.3735 | [7 empty] | 3214.3735
|  | HP | [11 empty] | 40
|  | OK | [10 empty] | HP Vent | 399.9965
|  |  | 28.3478 |  | 31.4181 |  | 15.4476 |  | 10.9403 |  | 33.8513 |  | 1.4211e-14
27.0811
| 2.5241 | [13 empty] | 1087.426
|  |  | 30.872 |  |  | 31.4181 |  |  |  | 10.9403
|  |  | 2993.389 |  |  | 2985.206 |  |  |  | 3016.9381 |  |  |  | 2993.3964
|  | MP | [11 empty] | 11
|  | OK | [10 empty] | MP Vent | 274.3613
|  |  | 0 |  | 0 | [5 empty] | 73.2303 |  | 0
43.9382
| 0 | [13 empty] | 781.1977
|  |  | 0 |  |  | 0 |  | 15.4476 |  |  |  | 9.7622
|  |  | 2816.5996 |  |  | 2861.1836 |  | 2866.2397 |  |  |  | 2738.0566 |  | 2816.6022
|  | LP | [11 empty] | 4 |  | 71.0193
|  | OK | [10 empty] | LP Vent | 179.0474 |  | 897.9687
123.7293 |  |  | 6.8157 | [9 empty] | 18.3941
511.577 |  |  |  |  | 61.257
604.7235
|  |  | 118.1508 | [5 empty] | Economics | Price | Value | Total per hr
|  |  | 394.3723 |  |  | Make Up |  |  | Fuel | 800 | 7.0183 | 5614.6284
[6 empty] | 56.8938 |  |  | Water | 0.8 | 56.8938 | 45.515
[6 empty] | 167.889 |  |  | Power Buy | 1.5 | 0 | 0
[9 empty] | Power Sell | 2.5 | -3056.9249 | -7642.3123
[11 empty] | Total | -1982.1688
BT1
BT2
TG2
HP User
TG1
MP User
Blr 3
Blr 2
Blr 1
Blr 1
Blr 2
Blr 3

## Control
Model Control
Model Mode | MATLAB
Steam Demand | 120.0051
Total Cost | -1982.1688
MODEL SPECIFICATIONS |  |  |  |  | Base Case Point
Boilers | BLR 1 | BLR 2 | BLR 3 |  | Boilers | BLR 1 | BLR 2 | BLR 3
State | 1 | 1 | 1 |  | State | 1 | 1 | 1
Steam Mass Flow | 60.0025 | 40.0017 | 20.0008 |  | Steam Mass Flow | 40.0017 | 40.0017 | 40.0017
Efficiency | 92.57% | 92.57% | 92.57% |  | Efficiency | 88.54% | 89.97% | 91.44%
Turbo Generators | TG1 | TG2 |  |  | Turbo Generators | TG1 | TG2
State | 1 | 1 |  |  | State | 1 | 1
Shaftwork | 2000 | 1493.8391 |  |  | Shaftwork | 1000 | 500
Efficiency | 69.64% | 65.92% |  |  | Efficiency | 59.71% | 46.45%
Steam Turbines | BT1 | BT2 |  |  | Steam Turbines | BT1 | BT2
State | 1 | 0 |  |  | State | 1 | 0
Power | 600 | 200 |  |  | Power | 600 | 200
Efficiency | 60% | 60% |  |  | Efficiency | 60% | 60%
Steam Users | HP User | MP User |  |  | Steam Users | HP User | MP User
Duty | 20000 | 45000 |  |  | Duty | 10000 | 15000
Return Fraction | 0.8 | 0.6 |  |  | Return Fraction | 0.8 | 0.6
Prices | Fuel Gas | Buy Elec | Sell Elec | Water | Prices | Fuel Gas | Buy Elec | Sell Elec | Water
$ per unit | 800 | 1.5 | 2.5 | 0.8 | $ per unit | 800 | 0.27 | 0.2 | 0.8
Simulation Optimal Point Import
[5 empty] | Boilers | BLR 1 | BLR 2 | BLR 3
[5 empty] | State | 1 | 1 | 1 |  | Sum
[5 empty] | Fraction | 0.53066 | 0.28796 | 0.18138 |  | 1
[5 empty] | Steam Mass Flow | 63.6818 | 34.5572 | 21.7661
[5 empty] | Efficiency | 89.3% | 88.5% | 89.38%
[5 empty] | Turbo Generators | TG1 | TG2
[5 empty] | State | 1 | 0
[5 empty] | Shaftwork | 595.0968 | 0
[5 empty] | Efficiency | 50% | 1e-06%
[5 empty] | Steam Turbines | BT1 | BT2
[5 empty] | State | 1 | 0
[5 empty] | Power | 600 | 200
[5 empty] | Efficiency | 60% | 60%
[5 empty] | Steam Users | HP User | MP User
[5 empty] | Duty | 10000 | 15000
[5 empty] | Return Fraction | 0.8 | 0.6
[5 empty] | Prices | Fuel Gas | Buy Elec | Sell Elec | Water
[5 empty] | $ per unit | 800 | 0.27 | 0.2 | 0.8

## MATLAB
MATLAB Import
Boilers | BLR 1 | BLR 2 | BLR 3
State | 1 | 1 | 1 |  | Sum | Model Error
Steam Mass Flow | 60 | 40 | 20 |  | 120 | 0.004231%
Efficiency | 92.57% | 92.57% | 92.57%
Turbo Generators | TG1 | TG2
State | 1 | 1
Shaftwork | 2000 | 1493.8391
Efficiency | 69.64% | 65.92%
Steam Turbines | BT1 | BT2
State | 1 | 0
Power | 600 | 200
Efficiency | 60% | 60%
Steam Users | HP User | MP User
Duty | 20000 | 45000
Return Fraction | 0.8 | 0.6
Prices | Fuel Gas | Buy Electricity | Sell Electricity | Water
$ per unit | 800 | 1.5 | 2.5 | 0.8

## Producers
Producers
Steam Demand: | 120.0051
Boilers | BLR 1 | BLR 2 | BLR 3
State | 1 | 1 | 1
Min | 20 | 10 | 5
Max | 60 | 40 | 20 | Sum
Current | 60.0025 | 40.0017 | 20.0008 | 120.0051
BFW Enthalpy | 511.577 | 511.577 | 511.577
Steam Mass Flow | 60.0025 | 40.0017 | 20.0008
Steam Temperature | 400 | 400 | 400
Steam Pressure | 40 | 40 | 40
Blowdown Ratio | 0.01 | 0.01 | 0.01
Firing Efficiency | 92.57% | 92.57% | 92.57%
Steam Enthalpy | 3214.3735 | 3214.3735 | 3214.3735
BFW Mass Flow | 60.6026 | 40.4017 | 20.2009
Blowdown Mass Flow | 0.60003 | 0.40002 | 0.20001
Blowdown Enthalpy | 1087.426 | 1087.426 | 1087.426
Duty | 48766.0437 | 32510.6958 | 16255.3479
Fuel Mass Flow | 3.5091 | 2.3394 | 1.1697
Total Steam Flow | 120.0051
Total BFW Mass Flow | 121.2051
Total Duty | 97532.0875
Fuel NHV | 50028.6733

## Turbines
Turbines
| Turbines | TG1 | TG2 | BT1 | BT2
| State | 1 | 1 | 1 | 0
| Max Shaftwork | 2000 | 2000 | 600 | 200
| Inlet Enthalpy | 3214.3735 | 3214.3735 | 3214.3735 | 2993.3964
| Inlet Pressure | 40 | 40 | 40 | 11
| Outlet Pressure | 11 | 4 | 11 | 4
| Efficiency | 69.64% | 65.92% | 60% | 60%
| Power | 2000 | 1493.8391 | 600 | 0
| Outlet Mass Flow | 31.4181 | 15.4476 | 10.9403 | 0
| Outlet Enthalpy | 2985.206 | 2866.2397 | 3016.9381 | 2861.1836
| Power Balance | 3056.9249

## JSteamHidden
Units
Pressure | bar | OK
Temperature | C | OK
MassFlow | tonne/hr | OK
MoleFlow | kmol/hr | OK
Power | kW | OK
Energy | kJ | OK
Mass | kg | OK
Mole | kmol | OK
Volume | m3 | OK
Viscosity | uPa.s | OK
ThermalConductivity | mW/(m.K) | OK
Basis | mass | OK

## PlantEquip
Plant Equipment
| Desuperheaters | HP-MP | MP-LP | FlashDrum
| Steam Enthalpy | 3214.3735 | 2993.3964 | Operating Pressure | 4
| Water Enthalpy | 511.577 | 511.577 | Inlet Enthalpy | 897.9687
| Outlet Pressure | 11 | 4 | Inlet Mass Flow | 71.0193
| Outlet Temperature | 274.3613 | 179.0474 | Vapour Mass Flow | 9.7622
| Outlet Mass Flow | 30.872 | 0 | Vapour Enthalpy | 2738.0566
| Water Mass Flow | 2.5241 | 0 | Liquid Mass Flow | 61.257
| Steam Mass Flow | 28.3478 | 0 | Liquid Enthalpy | 604.7235
| Outlet Enthalpy | 2993.389 | 2816.5996
| Deaerator |  |  | Pump
| Operating Pressure | 2 |  | Inlet Enthalpy | 504.6838
| Steam Enthalpy | 2816.6022 |  | Inlet Pressure | 2
| Water Enthalpy | 394.3723 |  | Inlet Mass Flow | 123.7293
| Liquid Mass Flow | 123.7293 |  | Outlet Pressure | 47
| Vent Ratio | 0.01 |  | Efficiency | 70%
| Steam Mass Flow | 6.8157 |  | Outlet Enthalpy | 511.577
| Water Mass Flow | 118.1508 |  | Power | 236.9142
| Liquid Enthalpy | 504.6838
| Vapour Mass Flow | 1.2373

## Compositions
Fuel Compositions | [12 empty] | Do not modify sheet name or layout
Fuel Name |  | Fuel_1 2 | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Status |  | OK | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME? | #NAME?
Description |  | 100% Methane
Basis |  | Mole Fraction | Mole Fraction | Mole Fraction | Mole Fraction | Mole Fraction | Mole Fraction | Mole Fraction | Mole Fraction | Mole Fraction | Mole Fraction | Mole Fraction | Mole Fraction
Hydrocarbons
Methane | CH4 | 100
Ethylene | C2H4
Ethane | C2H6
Propylene | C3H6
Propane | C3H8
IsoButene | iC4H8
n-Butane | C4H10
IsoButane | iC4H10
n-Pentane | C5H12
IsoPentane | iC5H12
n-Hexane | C6H14
Other Combustibles
Hydrogen | H2
Carbon Monoxide | CO
Inerts & Non-Combustibles
Carbon | C
Carbon Dioxide | CO2
Nitrogen | N2
Oxygen | O2
Water | H2O
Sulfurous
Hydrogen Sulfide | H2S
Sulfur Dioxide | SO2
Composition Sum |  | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0